ENGINEER SPECIFICATION GUIDE

Oil Separators, Solids Interceptors, Chemical Waste Tanks

Striem provides the specification language below to assist in the specification of our products, including oil separators, solids interceptors, chemical waste tanks, and monitoring solutions.

NOTES:

Black: Insert directly into project specification Section 22 40 00 - Plumbing Fixtures or where appropriate.

Blue: Included in this document to assist you and is not to be included in the specification language.

Red: Optional accessories or equipment applicable to the product and available to specify at your discretion.

PART 1 - GENERAL

Insert the following paragraphs under “Submittals”:

A.	Review Submittals:

1.	Product Data: Manufacturer’s standard data sheets describing components including materials, dimensions, relationship to adjacent construction, and attachments.

PART 2 - PRODUCTS

Insert the following under “Manufacturers”. Edit to indicate whether substitutions will be permitted for the products in this section.

A.	Contract Documents are based on products by Striem, Kansas City, KS USA

B.	Substitutions: [Under provisions of Division 01.] [Not permitted.]

Insert the following under “Components.” Refer to Striem’s website for part numbers and specifications, then select and edit the following paragraphs accordingly. All red text represents optional items, include as necessary.

OIL SEPARATORS

Include the following for an oil separator for all applications – indoor or outdoor, above or below grade.

A.	Oil Separator:

1.	Model: High Efficiency Oil/Water Separator Series Model No. OS-25, OS-50, OS-75, OS-100, OS-350, OS-500

2.	Striem high efficiency oil/water separator model ____ shall be lifetime guaranteed and made in the USA. Separator shall be certified to IAPMO IGC 325 and carry a UPC listing. Separator shall be constructed of polyethylene. Separator shall be manufactured for above- or below-grade installation. Field-adjustable riser system is available as an option to bring manhole cover to grade. Separator flow rate shall be ___ GPM. Separator liquid holding capacity shall be __ gallons and oil capacity shall be ___ gallons. Solids capacity shall be ___ gallons. Cover shall provide water/gastight seal and have a maximum _____ lbs. load capacity.

**** OR ****

A.	Oil Separator:

1.	Model: Oil Tanker™ Series Model No. OT-750, OT-1000, OT-1500, OT-2000

2.	Description: Striem oil separator model _____ shall be lifetime guaranteed and made in the USA. Separator shall be constructed of polyethylene. Separator shall be manufactured for below-grade installation. Field-adjustable riser system is available as an option to bring manhole covers to grade. Separator flow rate shall be 314 GPM. Separator liquid holding capacity shall be ___ gallons and oil capacity shall be ___ gallons. Solids capacity shall be ___ gallons. Covers shall be H20 rated pickable cast iron. Separator shall be certified to IAPMO IGC 183-2016 and carry a UPC listing.

Include the following for an oil separator with oil level monitoring, for all applications – indoor or outdoor, above or below grade.

A.	Oil Separator with oil level monitoring:

1.	Model: Slick Stick™ Oil Level Monitoring System. OS-50-SS, OS-75-SS, OS-100-SS, OS-350-SS, OS-500-SS, OT-750-SS, OT-1000-SS, OT-1500-SS, OT-2000-SS

2.	Description: Striem Slick Stick™ oil level monitoring system model # ____ shall be lifetime guaranteed and made in the USA. Separator shall be constructed of polyethylene. Separator shall be furnished for above or below grade installation. Field-adjustable riser system is available as an option to bring manhole covers to grade. Separator flow rate shall be ___ GPM. Separator liquid holding capacity shall be ___ gallons and oil capacity shall be ____ gallons.Solids capacity shall be ___ gallons. Cover shall provide water/gas-tight seal and have minimum ____ lbs. load capacity. The Slick Stick™ audio / visual alarm provides warning of high oil level conditions within separator via an interface float. Unit comes supplied with extra dry contact for connection to a building alarm system. Single phase, 120-volt, 60 hertz power required. NEMA 4X fiberglass, corrosion resistant, weatherproof enclosure suitable for outdoor use and damp environments.

SOLIDS INTERCEPTORS

Include the following for a solids interceptor for indoor, point-of-use, under counter or in-line drainage (versus surface drainage) applications, including application for hair/lint/food waste/clay and plaster.

A.	Interceptor:

1.	Model: SIDEKICK

2.	Description: Striem solids interceptor model SIDEKICK shall be lifetime guaranteed and made in the USA. Interceptor shall be constructed of an injection molded PVC housing and polycarbonate perforated basket. Interceptor shall be certified to IAPMO/ANSI/CAN Z1167 and carry a UPC listing. Interceptor is manufactured for above-grade installation. Basket shall provide the ability for side-access maintenance and shall be clear to allow visibility into unit. Solids capacity shall be 0.17 gallons. Optional tamper proof model # Sidekick-TP.

Include the following for a solids interceptor for all in-line drainage (versus surface drainage) applications – indoor or outdoor, above or below grade, including applications for food waste from disposers, hair, lint, etc.

A.	Interceptor:

1.	Model: The Aardvark™ Model AA-2, AA-3, AA-4, AA-6

2.	Description: Striem AA-__ solids interceptor shall be lifetime guaranteed and made in the USA. Interceptor shall be constructed of polyethylene. Interceptor shall be certified to IAPMO/ANSI/CAN Z1167 and carry a UPC listing. Interceptor shall be furnished for above- or below-grade installation. Field-adjustable riser system is available as an option to bring manhole cover to grade. Interceptor shall have removable, corrosion-resistant filter basket. Interceptor shall be equipped with high and low outlet options. Filter basket solids capacity shall be 7 gallons. Cover shall be water/gas-tight with a minimum 2,000 lbs. load capacity. Optional: Anchor flange for high water table installations.

**** OR ****

A.	Interceptor:

1.	Model: Prospector™ Series Model PS-25-S, PS-50-S, or PS-275-S

2.	Description: Striem solids interceptor model _____ shall be lifetime guaranteed and made in the USA. Interceptor shall be constructed of polyethylene. Interceptor shall be manufactured for above- or below-grade installation. Field-adjustable riser system is available as an option to bring manhole cover to grade. Interceptor shall have corrosion-resistant removable filter screen with 1/4" perforations. Interceptor liquid holding capacity shall be __ gallons and solids capacity shall be __ gallons. Cover shall provide water/gas-tight seal and have a maximum ____ lbs. load capacity.

Include the following for a solids interceptor for all surface drainage (versus in-line drainage) applications – indoor or outdoor, below grade, including application for sand/oil, parking lots, carwashes, and other interception of surface drainage debris.

A.	Interceptor:

1.	Model: Settler™ Series Model CB-50-S, CB-125-S or CB-275-S, CB-500-S, CB-750-S, CB-1000-S,  CB-1500-S, CB-2000-S

2.	Description: Striem solids interceptor model _____ shall be lifetime guaranteed and made in the USA. Interceptor shall be constructed of polyethylene. Interceptor shall be manufactured for above- or below-grade installation. Field-adjustable riser system is available as an option to bring manhole covers to grade. Interceptor liquid holding capacity shall be ___ gallons and solids capacity shall be ___ gallons. Covers shall provide water/gastight seal and have a maximum 16,000 lbs. load capacity

**** OR ****

A.	Interceptor:

1.	Model: Settler™ Series Model CB-50-G or CB-125-G, CB-500-G

2.	Description: Striem solids interceptor model _____ shall be lifetime guaranteed and made in the USA. Interceptor shall be constructed of polyethylene. Interceptor shall be manufactured for below-grade installation. Field adjustable riser system is available as an option to bring manhole cover to grade. Interceptor liquid holding capacity shall be ___ gallons. Interceptor solids capacity shall be ___ gallons. BCB-7 basket solids capacity shall be 7 gallons. Cover shall be H20 rated cast iron grate.

A.	Interceptor:

1.	Model: Settler™ Series Model SI-UPC-1016

2.	Description: Striem sand interceptor model SI-UPC-1016 shall be lifetime guaranteed and made in the USA. Interceptor shall be constructed of polyethylene. Interceptor shall be manufactured for above- or below-grade installation. Field-adjustable riser system is available as an option to bring manhole covers to grade. Interceptor liquid holding capacity shall be 250 gallons. BCB-7 basket solids capacity shall be 7 gallons. Interceptor shall have a cast iron grate over inlet section, and pickable cast iron cover over outlet section. Each cover shall be H20 rated.

DRAIN TROUGH

Include the following for any applications involving discharge from washing machine(s) where lint and solids are required to be intercepted before entering the sanitary system. Applications include On-Premise Laundry (hotels, dorms, fire houses / police stations, high schools, and nursing homes), and Vended Laundry (coin laundromat/washateria).

Drain Trough:

1.	Model: Tuff Trough™ Series Model TT-3, TT-6, TT-10

2.	Description: Striem Tuff Trough shall be lifetime guaranteed and made in the USA. Trough shall be constructed of polyethylene with ¼” nominal wall thickness. Trough shall have removable, corrosion-resistant primary filter screen and secondary filter screen. Trough shall be furnished with a nested cover, internally sloped floor, and suitable for above- or below-grade installation. Trough shall be equipped with a plain end molded outlet. Inlet connections are field installed. Maximum operating temperature 165°F intermittent. Trough shall be certified to IAPMO/ANSI/CAN Z1167 and carry a UPC listing.

CHEMICAL WASTE TANKS

Include the following for all indoor, point-of-use or under counter acid neutralization tank applications (one tank for each lab station).

A.	Acid Neutralization Tank:

1.	Model: Lab Rat™ Series Model LB-2 or LB-5

2.	Description: Striem neutralization tank model ___ shall be lifetime guaranteed and made in the USA. Tank shall be constructed of polyethylene. Tank shall be manufactured for above-grade installation. Tank shall be furnished with (2) inlets and (1) outlet connection with bushings included to field-adapt to 1-1/2" or 2" drain line pipe size. Tank shall be water-tight up to 36" head and contain an internal sewer gas trap. Tank shall have gasketed cover with captive hand-thread hardware.

Optional: Use Striem limestone chips 2” - 3” in size with a calcium carbonate content (CACO3) of 90% or greater. Model # LS-50.

**** OR ****

A.	ADA Acid Neutralization Tank:

1.	Model: Lab Rat™ Series Model LB-2-ADA

2.	Description: Striem neutralization tank model LB-2-ADA shall be lifetime guaranteed and made in the USA. Tank shall be constructed of polyethylene. Tank shall be manufactured for above-grade installation. Tank shall be furnished with (2) inlets and (1) outlet connection with bushings included to field-adapt to 1-1/2" or 2" drain line pipe size. Tank shall be watertight up to 36" head and contain an internal sewer gas trap. Tank shall have gasketed cover.

Optional: Use Striem limestone chips 2” - 3” in size with a calcium carbonate content (CACO3) of 90% or greater. Model # LS-50.

Include the following for any centralized acid neutralization tank applications, indoor or outdoor, above or below grade, including application for professional and teaching labs up to 75 lab stations (sinks) or 250 gallons liquid capacity, and industrial process neutralization.

A.	Acid Neutralization Tank:

1.	Model: Lab Basin™ Series Model LB-25, LB-50, LB-125 or LB-275, LB-500, LB-750, LB-1000,          LB-1500, LB-2000

2.	Description: Striem neutralization tank model _____ shall be lifetime guaranteed and made in the USA. Tank shall be constructed of polyethylene. Tank shall be manufactured for above- or below-grade installation. Field-adjustable riser system is available as an option to bring manhole cover to grade. Tank liquid holding capacity shall be ___ gallons. Cover shall provide water/gas-tight seal and have a maximum ____ lbs. load capacity.

Optional: Use Striem limestone chips 2” - 3” in size with a calcium carbonate content (CACO3) of 90% or greater.

Include the following for monitoring the pH of any waste stream or tank with one pH sensor, including acid waste lines in teaching and professional labs and industrial process. Command Center™ includes one pH sensor, monitoring/alarm panel, 50ft of sensor wire and a sensor cleaning and calibrating kit. Sensor placement kit (SPK) for installing the pH sensor is required but sold separately.

A.	pH Monitoring System

1.	Model: Command Center™ Model: CC-1

2.	Description: Command Center pH Monitor shall be furnished with audio/visual alarms, preprogrammed high/low pH limits, and logic to flush outlet line with fresh water as pH approaches high/low limits (solenoid and piping by others). Monitor shall include (2) SD cards for approximately 2 years of recording memory. Monitor shall be furnished with pH sensor maintenance kit containing sensor cleaning brush and solution, calibration buffer solutions, NEMA 4X lockable enclosure, and fully UL listed components.

Include the following for any decontamination holding tank applications, indoor or outdoor, above or below grade, including application for emergency wash down stations, battery changing stations, and industrial process surface drainage.

A.	Decontamination Holding Tank:

1.	Model: Bio Basin™ Series Model BB-275, BB-500, BB-750, BB-1000 or BB-1500, BB-2000

2.	Description: Striem decontamination tank model ______ shall be lifetime guaranteed and made in the USA. Tank shall be constructed of polyethylene. Tank shall be manufactured for above- or below-grade installation. Field-adjustable riser system is available as an option to bring manhole covers to grade. Tank liquid holding capactiy shall be _____ gallons. Covers shall provide water/gas-tight seal and have a maximum 16,000 lbs. load capacity.

Optional: add a single (AVA-3) or multi-level (AVA-4) float switch and alarm panel to monitor the tank liquid level. Optional manual or electronically actuated valves are available upon request.

SAMPLING PORTS

Include the following anywhere visual or sampling access is required to monitor effluent water quality before entering the public sewer system.

A.	Sampling Port:

1.	Model: Inspector™ Series Model Inspector-4 or Inspector-6

2.	Description: Striem sampling port model _______ shall be lifetime guaranteed and made in the USA. Sampling port shall be constructed of polyethylene. Sampling port shall be manufactured for above- or below-grade installation. Sampling port shall provide integral flow-capture feature for ease of sampling. Field-adjustable riser system is available as an option to bring manhole cover to grade. Cover shall provide water/gas-tight seal and have a maximum 16,000 lbs. load capacity.

PART 3 - EXECUTION

Include the following under “Installation”:

A.	Install components in accordance with manufacturer's instructions and approved product data submittals.